## Slide 1: WPSA – 2026 monitoring meeting Tools development in support of OP 2 magnets operation
ENEA - Chiarasole FIAMOZZI ZIGNANI, Gianluca DE MARZI
CEA - François BONNE, Quentin LE COZ
WPSA Monitoring Meeting – 13 October 13, 2026

## Slide 2: Task Specifications: 2024 & 2025
Developed tools include:
Jc parameterization and assessment of hysteresis loss in CEA experiments
Th simulations of EF coils
TF QDV data retrieval and manipulation
Symcryogenics: global FSD of the loop 2 magnets EF + CS
2024 and 2025 activities completed  deliverable uploaded and approved
2024
2025
SA-SE.CM.OP.06-T003-D001 «Simcryogenics model development for JT-60SA operation” (Francois Bonne)
SA-SE.OP.SSO.01-T007 “2025 Cryogenic models” (Francois Bonne)

## Slide 3: Task Specifications - 2026
Tools development in support of OP 2 magnets operation.
Update of the magnet THEA models (settings and code consolidation) in preparation of OP 2.
In order to improve the accuracy and reliability of THEA simulations, the Jc laws will be consolidated and cross-checked. Also, the updated friction factor correlations will be implemented in the models. The resulting Jc(B,T,ε) parameterization will be implemented in the THEA software, to update and consolidate the thermo-electro-magnetic models. The updated models, including the refined parameterization of the critical surface, will be used in quench simulations under different operational scenarios to assess hot-spot temperatures and thermal margins, related to OP 2.
Based on the 2025 activities where the expected behaviour of magnets of loop 2 (PFs) were calculated in case of global FSD at 20 kA current, we will calculate the profile of power that is going to be extracted by the bath. The deliverable will include comparison with loop 1 FSD to have a better understanding of what to expect from the bath/refrigerator point of view in the PF FSD case.
The TFQDV signal processing activities will be devoted to the validation and the consolidation of software tool (ANN-based) aimed at TFQDV signal retrieval, correction and transmission to TF interlock system.
2 PM shared between 2 institutes (1 PM each): CEA (F. Bonne, Q. Le Coz), ENEA (G. De Marzi, C. Fiamozzi Zignani)

## Slide 4: Parameterization of Nb3Sn Critical Surface
Consolidated and cross-checked the Jc parametrization, with the aim to establish a common framework between CEA and ENEA codes
The sign of m has changed to reflect the fact that it is a tensile strain
The implementation of Tc(B,) avoids field dependence to prevent circular definition.
Introduced a low field cut-off in the Jc formulation
Jc parametrization:
Parameter | Value |  | Units
 | Old (2025) | New | 
C | 35.0 | 35.0 | kAT/mm2
Bc20 | 30.7 | 30.7 | T
Tc0 | 16.8 | 16.8 | K
p | 0.5 | 0.5 | -
q | 2 | 2 | -
Ca1 | 47.6 | 47.6 | -
Ca2 | 6.4 | 6.4 | -
ε0,a | 0.273 | 0.273 | %
εm | -0.33 | +0.33 | %

## Slide 5: Cut-off in Low-Field Jc Scaling Law
To avoid divergence, a low field cut-off has been introduced
Icut-off, 4.2 K = 9.6 kA @ 80 mT

## Slide 6: Update on 2026 task activities
To avoid divergence, a low field cut-off has been introduced
Icut-off, 4.2 K = 9.6 kA @ 80 mT
Icut-off, 6 K = 7.8 kA @ 90 mT
Icut-off, 8 K = 5.9 kA @ 100 mT

## Slide 7: Update on TFQDV activities
The TFQDV signal processing activities has been devoted to the validation and the consolidation of software tool (ANN-based) aimed at TFQDV signal retrieval, correction and transmission to TF interlock system.
TFQDV signal processing activities
Real-time filtering achieved both in Matlab and C++
All UPF filtered

## Slide 8: The TFQDV signal processing activities
devoted to the validation and the consolidation of software tool (ANN-based) aimed at TFQDV signal retrieval, correction and transmission to TF interlock system
During Integrated Commissioning held in 2021 and 2023, it was observed that during PF current transients, a spurious transient signal was generated on the TF quench detection voltage (TFQDV) channels, that could be misinterpreted as a TF quench event  as the persistent risk of false-positive quench detection could penalize operation schedules, a dedicated mitigation strategy was implemented:
A software-based approach was chosen to correct in real-time the TFQDV signal through a correlation with a reference signal, for instance the PF coils control voltage (UPF).

## Slide 9: Two methods were pursued:
A purely linear correlation between TFQDV and UPF processed signals, using a direct transfer matrix  Unique Matrix (UM) approach
An Artificial Neuron Network (ANN)-based approach to dynamically correlate TFQDV and UPF to improve fitting fidelity  ANN approach
The quench identification criterion is based on a 1 second integration of the nine integrated TFQDV (intV) voltage channels
metric that reflects the correction performance, associated with the mitigation of false positive detection risk: Peak Attenuation Ratio (RPA) and is defined as RPA=max(|corrIntV|) / max(|IntV|) where the two components are identified as shown in Figure
Key concepts:

## Slide 10
The UM method:
demonstrates the ability to mitigate spurious IntV peaks, with 85% rate of shots showing lower maximum after correction. However, it remains limited as only about 20% of the shots exhibited an intV peak decreased by more than 25%, and the best correction rate is 38%
ANN approach:
    single inner layer architecture
    The considered ANN architecture is Multy Layer Perceptron (MLP) implemented in C++ environment with settings as follows:
    nb of input / hidden layers / output neurons: 100 /80 /9
    Learning rate: h=0.01; momentum coefficient: a=0.1
    Number of total epochs: 40000
the mathematical relationship that the ANN will approximate is of the type:
intVj(t)=f(VPFi(t-0.1s), VPFi(t-0.2s), …, VPFi(t-1s))
with i=1,…,10 indexing the 10 PF coils, and j=1,…9 indexing the 9 channels of the intV signals.
7 runs  selected to maximize the diversity of current patterns
substantial improvement with 80% of shots having peaks mitigated by more than 25%, and obtaining lower average RPA
C++ Real-time filtering

## Slide 11
    .
    four inner layers architecture
    explored different MLP architectures by considering four hidden layers (4‑HL) for which the number of neurons are 128, 64, 32 and 16.
    The activation function was changed from Sigmoid to LeakyReLU, for the hidden layers neurons, and a linear function for the output layer. The network was trained using Adam optimizer with a learning rate of 10-4 and the reduced number of training epochs was fixed to 3000
This approach was developed using the open source PyTorch framework
Integrated TFQDV curves before and after correction
A refined setting of the MLP configuration applied on selected OP1 shots was shown to reduce the quench identification signal peak by almost 70 % in average, and by almost 90% for the best cases.
These results are highly encouraging, and the applied method will be further optimized

## Slide 12: Othello test
Othello test facility at CEA.
Hydraulic characterization of conductor sample with gaseous nitrogen flow.
Pressure drop measurement to evaluate the friction factor.
3 CICC samples to be tested (EF-L, EF-H and CS) plus the central spiral.

## Slide 13: Conductor samples
Bundle (spiral blocked):
  EF-L, EF-H, CS → August 2025
Full conductor (bundle + spiral)
  EF-L → November 2025
  EF-H → March 2026
  CS → not done (difficulty to remove the spiral plug)
Spiral alone (same for all the conductors) → May 2026

## Slide 14: Hydraulic geometrical parameters
Reduction of the wetted perimeter by a factor of 5/6 accounting for the inter-strand contact.
 | Bundle - EF-H | Bundle - EF-L | Bundle - CS | Spiral
Dh [m] | 5.01E-04 | 4.90E-04 | 4.82E-04 | 0.009
S [m²] | 1.37E-04 | 9.88E-05 | 9.61E-05 | 6.3617E-05
The hydraulic diameter of the spiral is chosen as the outer diameter.

## Slide 15: Othello test – Spiral
Outer diameter of the spiral: 9 mm
Initial inner diameter of the tube: 10.42 mm
Tube crimped on the spiral

## Slide 16: Othello test – Spiral
Length between pressure taps: 1.5 m
1.5 m

## Slide 17: Othello test – Spiral
Reynolds number ~ Re = [ 28000 ; 350000 ]

## Slide 18: Othello test – Spiral
Reynolds number in operating conditions ~ 120000 (EF-H) – 150000 (EF-L)
Classical correlation for the spiral in the form of:
Best fit:
As b has a low value, f is weakly dependent on Re.
The correlation is consistent with the value of ~ 0.28 that was deduced from the tests of the bundle alone and the one with the full conductor.
The data are showing a non-monotonous plot.
A more refined correlation using a polynomial fit could be used.

## Slide 19: Othello test – EF-H
Best fit for the full conductor:

## Slide 20: Othello test – EF-L
Best fit for the full conductor:

## Slide 21: Conclusion of Othello activities
Test of the full conductors (bundle + spiral) for EF-H, EF-L and CS;
Unplugging of 2 of the 3 conductors (EF-L and EF-H), CS too difficult to unblock (deformation of the spiral);
Test of the central spiral alone.
Results consistent with the 2011 CEA test campaign (JL. Marechal);
Comparison with experimental data from the tokamak operation is on-going;
The numerical models (THEA) are being updated with the new correlations and used on different scenario (operation, quench events, cool-downs…).

## Slide 22: Update on 2026 task activities
Simcryogenics modeling of loop 2 : energy assessment and bath behavior
The global FSD of the loop 2 magnets EF + CS has been performed in 2025. Final checks will be done to verify that the energy deposited on the magnets in case of FSD in matching other code, and the behavior of the thermal buffer will be predicted.
Simcryogenics modeling of loop 2
Power, energy and current in case of PF magnet FSD

## Slide 23: 2027 Work Plan
On-site participation to OP2 envisaged (missions)
PMs for Jc vs strain measurements at ENEA

## Slide 24: Thanks for your attention